## UPS
Sr No | Template Name | UPS_RATING | UPS_TYPE | UPS_BATTERY_VOLT | UPS_BATTERY_CHARGE | UPS_BATTERY_CHARGE_MODE | UPS_PHASE1_OUT_VOLT | UPS_PHASE2_OUT_VOLT | UPS_PHASE3_OUT_VOLT | UPS_PHASE1_OUT_CURR | UPS_PHASE2_OUT_CURR | UPS_PHASE3_OUT_CURR | UPS_BATTERY_PERCENT | UPS_LOAD_PHASE | UPS_PERCENT
| object_name | UPS Ratting | UPS Type | UPS Battery Voltage | UPS Battery Charge | UPS Charge Mode | UPS Phase 1 Output Voltage | UPS Phase 2 Output Voltage | UPS Phase 3 Output Voltage | UPS Phase 1 Output Current | UPS Phase 2 Output Current | UPS Phase 3 Output Current | UPS Battery Percentage | UPS Load Phase-wise | UPS Percent
| footer_query | ¦> map(fn: (r) => ({ r with _value: r._value /100.0 }))\n ¦> last() | ¦> last() | ¦> last() | ¦> last() | ¦> last() | ¦> last() | ¦> last() | ¦> last() | ¦> last() | ¦> last() | ¦> last() | ¦> aggregateWindow(every: 1h, fn: last, createEmpty: false) | ¦> group(columns: [\"zone\"]) \n¦> aggregateWindow(every: 1h, fn: last, createEmpty: false) | ¦> last()\n ¦> group(columns: [\"panel_no\"], mode:\"by\") \n ¦> sum(column: \"_value\")
| object_unit | kVA | Phase | V |  |  | V | V | V | A | A | A |  | % | %
| object_min_thresh | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
| object_max_thresh | [5 empty] | 280 | 280 | 280 |  |  |  |  | 100 | 100
1 | Delta UPS | RKVA | RTYPE | BATTVOLT | BATTCHR | BATTMODE | OV1 | OV2 | OV3 | OC1 | OC2 | OC3 | BATTPER | PLOAD1, PLOAD2, PLOAD3 | PLOAD1, PLOAD2, PLOAD3
2 | some_model |  |  | BATV |  |  | OV |  |  | IV |  |  |  | PLOAD | PLOAD

## DG
Sr No | Template Name | FUEL_LEVEL | RUN_HOURS | KWH | FL_RH_KWH | DG_BATTERY_VOLTAGE | CURRENT_FUEL_LEVEL | PREVIOUS_MONTH_DG_USE | CURRENT_MONTH_DG_USE | TODAY_DG_USE | PREVIOUS_MONTH_DG_KWH | CURRENT_MONTH_DG_KWH | TODAY_DG_KWH | TOTAL_DG_RUN_HRS | DG_CONSUMPTION
| object_name | Fuel Level | Run Hours | KWH | Run Hours VS Fuel Level VS KWH | DG Battery Voltage | Current Fuel Level | Previous Month DG Use | Current Month DG Use | Today DG Use | Previous Month DG KWH | Current Month DG KWH | Today’s DG KWH | Total DG Run HRS | DG consumption
| footer_query |  |  |  | ¦> aggregateWindow(every: 1h, fn: last, createEmpty: false) | ¦> last() | ¦> last() | ¦> aggregateWindow(every: 1d, fn: last, createEmpty: false)\n¦> difference(nonNegative: false, columns: [\"_value\"])\n¦> sum() | ¦> aggregateWindow(every: 1d, fn: last, createEmpty: false)\n¦> difference(nonNegative: false, columns: [\"_value\"])\n¦> sum() | ¦> aggregateWindow(every: 1d, fn: last, createEmpty: false)\n¦> difference(nonNegative: false, columns: [\"_value\"])\n¦> last() | ¦> timeShift(duration: 330m, columns: [ \"_time\"])\n¦> aggregateWindow(every: 1mo, fn: last, createEmpty: false)\n¦> difference(nonNegative: false, columns: [\"_value\"]) | ¦> timeShift(duration: 330m, columns: [ \"_time\"])\n¦> aggregateWindow(every: 1mo, fn: last, createEmpty: false)\n¦> difference(nonNegative: false, columns: [\"_value\"]) | ¦> timeShift(duration: 330m, columns: [ \"_time\"])\n¦> aggregateWindow(every: 1d, fn: last, createEmpty: false)\n¦> difference(nonNegative: false, columns: [\"_value\"])\n¦> last() | ¦> last() | ¦> last()
| object_unit | L |  | kWh |  | V | L | hours | hours | hours | kWh | kWh | kWh | hours | kWh
| object_min_thresh |  |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| object_max_thresh |  |  |  |  | V: 30
1 | sedemac_gc1111 | LEVEL | HRS | KWH | HRS, KWH, LEVEL | BV | LEVEL | HRS | HRS | HRS | KWH | KWH | KWH | HRS | KWH
2 | DG_fuel_sensor_DHL | FL |  |  | FL | bar: 30 BV to 30 LEVEL
3 | Deepsea-4520-MK11 | FL | ERT | KWH | ERT, KWH, FL | BV | FL | ERT | ERT | ERT | KWH | KWH | KWH | ERT | KWH
4 | DG SGC 120/121 | LEVEL | HRS | DKWH | HRS, DKWH, LEVEL | BV | LEVEL | HRS | HRS | HRS | DKWH | DKWH | DKWH | HRS | DKWH

## ENERGY
Sr No | Template Name | POWER_FACTOR | FREQUENCY | MAX_KWH | LAST_KWH | PHASE_WISE_LOAD | VOLTAGE | MAIN_KWH | PRE_MON_MAIN_KWH | PRE_MON_DG_KWH | DG_KWH | CURR_WEEK_HOURLY | CURR_MONTH_DAILY | PRE_THREE_MONTH | LAST_AVG_VOLTAGE | LAST_AVG_CURRENT | MAX_POWER
| object_name | Power Factor | Frequency | Max KW | Last KW | Phase Wise Load | Voltage | Main KWH | Previous Month Main KWH | Previous Month DG KWH | DG KWH | Past 7 Days Hourly consumption | Current Month Daily consumption | Previous 3 Month consumption | Average Voltage | Average Current | Max Power
| footer_query | ¦> last() | ¦> last() | ¦> max() \n¦> map(fn: (r) => ({ r with _value: r._value / 1000.0 })) | ¦> last() \n¦> map(fn: (r) => ({ r with _value: r._value / 1000.0 })) | ¦> last() | ¦> aggregateWindow(every: 1h, fn: last, createEmpty: false) | ¦> aggregateWindow(every: 1mo, fn: spread, createEmpty: false) \n¦> sum() | ¦> aggregateWindow(every: 1mo, fn: spread, createEmpty: false) \n¦> sum() | ¦> aggregateWindow(every: 10m, fn: last, createEmpty: false)\n¦> difference(nonNegative: false, columns: [\"_value\"])\n¦> map(fn: (r) => ({ r with _value: if r._value < 0 or r._value > 1000 then float(v:0) else float(v: \"${r._value}\"),}))\n¦> aggregateWindow(every: 1mo, fn: sum, createEmpty: false)\n¦> group(columns: [\"panel_no\"] ) | ¦> aggregateWindow(every: 10m, fn: last, createEmpty: false)\n¦> difference(nonNegative: false, columns: [\"_value\"])\n¦> map(fn: (r) => ({ r with _value: if r._value < 0 or r._value > 1000 then float(v:0) else float(v: \"${r._value}\"),}))\n¦> aggregateWindow(every: 1mo, fn: sum, createEmpty: false)\n¦> group(columns: [\"panel_no\"] ) | ¦> aggregateWindow(every: 1h, fn: spread, createEmpty: false) \n¦> sum() | ¦> aggregateWindow(every: 1d, fn: spread, createEmpty: false)\n ¦> sum() | ¦> aggregateWindow(every: 1mo, fn: spread, createEmpty: false) \n¦> sum() | ¦> last() | ¦> last() | ¦> max() \n¦> map(fn: (r) => ({ r with _value: r._value / 1000.0 }))
| object_unit |  | Hz | kW | kW | A | V | kWh | kWh | kWh | kWh |  |  |  | V | A | kW
| object_min_thresh | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| object_max_thresh | 1 | Hz: 50; V: 280 |  |  |  | 280 |  | 1000
1 | Elmeasure Energy Meter(Distribution) | APF | F | TKW | TKW | I1, I2, I3 | V1N, V2N, V3N, AVLN | WHIMP | WHIMP | WHEXP | WHEXP | WHIMP | WHIMP | WHIMP | AVLN | AI | TKW
2 | Elmeasure Energy Meter(Mains) | APF | F | TKW | TKW | I1, I2, I3 | V1N, V2N, V3N | WHIMP | WHIMP | WHEXP | WHEXP | WHIMP | WHIMP | WHIMP | AVLN | AI | TKW
3 | selec-306-C-D | APF | F | TKW | TKW | I1, I2, I3 | V1N, V2N, V3N | KWH | KWH | DKWH | DKWH | KWH | KWH | KWH | AVLN | AI | TKW
4 | selec-mrj4m-quad | APF | F | TKW | TKW | I1, I2, I3 | V1N, V2N, V3N | TKWH | TKWH | DKWH | DKWH | TKWH | TKWH | TKWH | AVLN | AI | TKW
5 | Schneider-Conzerv-METSEEM6438H | APF | F | TKW | TKW |  |  | KWHEXP | KWHEXP | KWHIMP | KWHIMP | KWHEXP | KWHEXP | KWHEXP |  |  | TKW
6 | schneider-em6400ng | APF | FREQ | TKW | TKW | I1, I2, I3 | V1, V2, V3 | KWH | KWH |  |  | KWH | KWH | KWH | LLVAVG | IAVG | TKW
7 | socomec-multis-lm35 | APF | F | kW1, kW2, kW3 | kW1, kW2, kW3 | I1, I2, I3 | V1N, V2N, V3N | KWH | KWH |  |  | KWH | KWH | KWH | AVLN | AI | kW1, kW2, kW3
8 | trinity-tinypro-6 | APF | F | TKW | TKW | I1, I2, I3 | V1N, V2N, V3N | KWH | KWH | DKWH1 | DKWH1 | KWH | KWH | KWH | AVLN | AI | TKW
9 | selec-mfm384 | APF | F | TKW | TKW | I1, I2, I3 | V1N, V2N, V3N | KWH | KWH |  |  | KWH | KWH | KWH | AVLN | AI | TKW
10 | selec-mfm384d | APF | F | TKW | TKW | I1, I2, I3 | V1N, V2N, V3N | KWH | KWH | DKWH | DKWH | KWH | KWH | KWH | AVLN | AI | TKW
11 | DT-108 |  | FREQ | KWH1, KWH2, KWH3 | KWH1, KWH2, KWH3 | I1, I2, I3 | VLN1, VLN2, VLN3 | KWH | KWH |  |  | KWH | KWH | KWH |  |  | KWH1, KWH2, KWH3
12 | LG5310 | APF | FREQ | TKW | TKW | I1, I2, I3 | V1N, V2N, V3N | KWH | KWH |  |  | KWH | KWH | KWH | AVLN | AI | TKW
13 | ELite 440 | APF | F | TKW | TKW | I1, I2, I3 | V1N, V2N, V3N | IMPKWH | IMPKWH | EXPKWH | EXPKWH | IMPKWH | IMPKWH | IMPKWH | AVLN |  | TKW
14 | ESP ModBus | APF | F | TKW | TKW | I1, I2, I3 | V1N, V2N, V3N | KWH | KWH | DKWH | DKWH | KWH | KWH | KWH | AVLN | AI | TKW
15 | Selec-EM4M-3P-C-100A | APF | F | TKW | TKW | I1, I2, I3 | V1N, V2N, V3N | TKWHMAIN | TKWHMAIN | TKWHDG | TKWHDG | TKWHMAIN | TKWHMAIN | TKWHMAIN | AVLN | I3 | TKW
16 | ELite 500 | APF | F | TKW | TKW | I1, I2, I3 | V1N, V2N, V3N | IMPKWH | IMPKWH | EXPKWH | EXPKWH | IMPKWH | IMPKWH | IMPKWH | AVLN |  | TKW

## FRESH_AIR
Sr No | Template Name | ON_OFF_STATUS
| object_name | ON/OFF status
| footer_query | ¦> aggregateWindow(every: 1d, fn: last, createEmpty: false)\n ¦> last()
object_unit
object_min_thresh
object_max_thresh
1 | 485 Based 8-IO | IOIN1, IOIN2, IOIN3, IOIN4, IOIN5, IOIN6, IOIN7, IOIN8

## MAIN_DASHBOARD
Sr No | Template Name | SITE_CARBON_FOOTPRINT | SITE_SAVINGS | SITE_EPI | SITE_AQI | SITE_AVG_OCCUPANCY | SITE_FEEL_TEMPERATURE | ENERGY_CONSUMPTION_ACT_VAL | DIESEL_CONSUMPTION_ACT_VAL | SITE_HISTORICAL_CONSUMPTION | SITE_ALERTS
| object_name | Previous Month Carbon Footprint Saved | Previous Month Saving | Previous Month EPI | AQI | Panel Status | Feel Temperature | Energy | Diesel | Last 3 Month energy consumption
| footer_query | ¦> aggregateWindow(every: 1mo, fn: spread, createEmpty: false)\n ¦>sum() | ¦> aggregateWindow(every: 1mo, fn: spread, createEmpty: false)\n ¦>sum() | ¦> aggregateWindow(every: 1mo, fn: spread, createEmpty: false)\n ¦>sum() | ¦> last() | ¦> last() | ¦> filter(fn: (r) => r._value > 0 and r._value < 150, onEmpty: \"keep\")\n ¦> group(columns: [\"_measurement\"])\n ¦> mean(column: \"_value\")\n | ¦> aggregateWindow(every: 1mo, fn: spread, createEmpty: false) \n¦> sum() | ¦> aggregateWindow(every: 1d, fn: last, createEmpty: false)\n ¦> difference(nonNegative: false, columns: [\"_value\"])\n ¦> sum(column: \"_value\") | ¦> aggregateWindow(every: 1mo, fn: spread, createEmpty: false) \n¦> sum()
| object_unit | kg | Kwh | kWh/sqft | % |  | °C
object_min_thresh
object_max_thresh
| baseline | 31500 | 35000 | 44080
| multiplier | 0.9
1 | Elmeasure Energy Meter(Distribution) | WHIMP | WHIMP | WHIMP |  |  |  | WHIMP | WHEXP | WHIMP
2 | Elmeasure Energy Meter(Mains) | WHIMP | WHIMP | WHIMP |  |  |  | WHIMP | WHEXP | WHIMP
3 | selec-306-C-D | KWH | KWH | KWH |  |  |  | KWH | KWH | KWH
4 | selec-mrj4m-quad | TKWH | TKWH | TKWH |  |  |  | TKWH | TKWH | TKWH
5 | Schneider-Conzerv-METSEEM6438H | KWHEXP | KWHEXP | KWHEXP |  |  |  | KWHEXP | KWHEXP | KWHEXP
6 | schneider-em6400ng | KWH | KWH | KWH |  |  |  | KWH |  | KWH

## MAIN_ENERGY_REPORT_WEEKLY
Sr No | Template Name | VOLTAGE | V1N | V2N | V3N | AVLN | POWER_FACTOR | ENERGY_KWH | Feel_Temp | ENERGY_MAX_KW | RKVA | BATTVOLT | PLOAD1 | PLOAD2 | PLOAD3 | DG_KWH | UPS_HIGH_USAGE | UPS_AVG_USAGE
| object_name | Voltage | Voltage | Voltage | Voltage | Voltage | Power Factor | KWH | Temperature | Energy Max KW | [5 empty] | DG KWH | UPS Highest Usage | UPS Average Usage
| footer_query | ¦> aggregateWindow(every: 1d, fn: last, createEmpty: false)\n ¦> last() | ¦> aggregateWindow(every: 1d, fn: last, createEmpty: false)\n ¦> last() | ¦> aggregateWindow(every: 1d, fn: last, createEmpty: false)\n ¦> last() | ¦> aggregateWindow(every: 1d, fn: last, createEmpty: false)\n ¦> last() | ¦> aggregateWindow(every: 1d, fn: last, createEmpty: false)\n ¦> last() | ¦> filter(fn: (r) => r._value > 0.85, onEmpty: \"keep\")\n ¦> aggregateWindow(every: 1mo, fn: mean, createEmpty: false) \n ¦> mean() | ¦> aggregateWindow(every: 1mo, fn: spread, createEmpty: false) \n¦> sum() | ¦> filter(fn: (r) => r._value > 0 and r._value < 150, onEmpty: \"keep\") \n¦> group(columns: [\"device_code\"])\n ¦> aggregateWindow(every: 1d, fn: mean, createEmpty: false) | ¦> max() \n¦> map(fn: (r) => ({ r with _value: r._value / 1000.0 })) | ¦> aggregateWindow(every: 1d, fn: last, createEmpty: false)\n ¦> last() \n ¦> map(fn: (r) => ({ r with _value: r._value / 100.0 })) | ¦> aggregateWindow(every: 1d, fn: last, createEmpty: false)\n ¦> mean() | ¦> aggregateWindow(every: 1d, fn: last, createEmpty: false)\n ¦> mean() | ¦> aggregateWindow(every: 1d, fn: last, createEmpty: false)\n ¦> mean() | ¦> aggregateWindow(every: 1d, fn: last, createEmpty: false)\n ¦> mean() | ¦> aggregateWindow(every: 1d, fn: last, createEmpty: false)\n ¦> difference(nonNegative: false, columns: [\"_value\"]) \n ¦> sum() | ¦> filter(fn: (r) => r._value > 0, onEmpty: \"keep\")\n ¦> aggregateWindow(every: 1d, fn: max, createEmpty: false)\n ¦> map(fn: (r) => ({ r with _value: r._value * 80.0 / 100.0})) | ¦> filter(fn: (r) => r._value > 0, onEmpty: \"keep\")\n ¦> aggregateWindow(every: 1d, fn: mean, createEmpty: false)\n ¦> map(fn: (r) => ({ r with _value: r._value * 80.0 / 100.0}))
| object_unit | V | V | V | V | V |  | kW | °C | kW | kVA | V | V | V | V | kWh
object_min_thresh
object_max_thresh
1 | Elmeasure Energy Meter(Distribution) | V1N, V2N, V3N, AVLN | V1N | V2N | V3N | AVLN | APF | kW: WHIMP; kW: TKW; kWh: WHEXP
2 | Elmeasure Energy Meter(Mains) | V1N, V2N, V3N | V1N | V2N | V3N | V1N, V2N, V3N | APF | kW: WHIMP; kW: TKW; kWh: WHEXP
3 | selec-306-C-D |  | V1N | V2N | V3N |  | APF | kW: KWH; kW: TKW; kWh: DKWH
4 | selec-mrj4m-quad |  | V1N | V2N | V3N |  | APF | kW: TKWH; kW: TKW; kWh: DKWH
5 | Schneider-Conzerv-METSEEM6438H | [5 empty] | APF | kW: KWHEXP; kW: TKW; kWh: KWHIMP
6 | schneider-em6400ng | V1, V2, V3 | V1 | V2 | V3 | V1, V2, V3 | APF | kW: KWH; kW: TKW
7 | Delta UPS | [6 empty] | kVA: RKVA; V: BATTVOLT; V: PLOAD1; V: PLOAD2; V: PLOAD3 | PLOAD | PLOAD
8 | some_model | [6 empty] | V: BATV; V: PLOAD | PLOAD | PLOAD

## MAIN_ENERGY_REPORT_MONTHLY
Sr No | Template Name | ENERGY_KWH | ENERGY_MAX_KW | POWER_FACTOR | MAX_KWH | RKVA | DG_RUN_HOURS | DG_KWH | Feel_Temp | HIGH_MAIN_VOLT_COUNT | LOW_MAIN_VOLT_COUNT | P_F_COUNT | UPS_BATT_ALERT | UPS_BATT_VOLT | UPS_HIGH_USAGE | UPS_AVG_USAGE
| object_name | KWH | Energy Max KW | Power Factor | Max KW |  | Run Hours | DG KWH | Temperature | High Mains Voltage Count | Low Mains Voltage Count | P.F Alert Count | UPS Battery Alert | UPS Battery Voltage | UPS Highest Usage | UPS Average Usage
| footer_query | ¦> aggregateWindow(every: 1mo, fn: spread, createEmpty: false) \n¦> sum() | ¦> max() \n¦> map(fn: (r) => ({ r with _value: r._value / 1000.0 })) | ¦> filter(fn: (r) => r._value > 0.85, onEmpty: \"keep\")\n ¦> aggregateWindow(every: 1mo, fn: mean, createEmpty: false) | ¦> max() \n¦> map(fn: (r) => ({ r with _value: r._value / 1000.0 })) | ¦> aggregateWindow(every: 1d, fn: last, createEmpty: false)\n ¦> last() \n ¦> map(fn: (r) => ({ r with _value: r._value / 100.0 })) |  | ¦> aggregateWindow(every: 10m, fn: last, createEmpty: false)\n¦> difference(nonNegative: false, columns: [\"_value\"])\n¦> map(fn: (r) => ({ r with _value: if r._value < 0 or r._value > 1000 then float(v:0) else float(v: \"${r._value}\"),}))\n¦> aggregateWindow(every: 1mo, fn: sum, createEmpty: false)\n¦> group(columns: [\"panel_no\"] ) | ¦> filter(fn: (r) => r._value > 0 and r._value < 150, onEmpty: \"keep\") \n¦> group(columns: [\"device_code\"])\n ¦> aggregateWindow(every: 1mo, fn: mean, createEmpty: false) | ¦> aggregateWindow(every: 10m, fn: last, createEmpty: false)\n ¦> filter(fn: (r) => r._value > 260, onEmpty: \"keep\")\n ¦> count(column: \"_value\") | ¦> aggregateWindow(every: 10m, fn: last, createEmpty: false)\n ¦> filter(fn: (r) => r._value < 180, onEmpty: \"keep\")\n ¦> count(column: \"_value\") | ¦> hourSelection(start: 8, stop: 18)\n ¦> filter(fn: (r) => r._value > -0.85 and r._value < 0.85, onEmpty: \"keep\")\n ¦> aggregateWindow(every: 10m, fn: count, createEmpty: false)\n ¦> sum(column: \"_value\")\n | ¦> aggregateWindow(every: 10m, fn: last, createEmpty: false)\n ¦> filter(fn: (r) => r._value < 221, onEmpty: \"keep\")\n ¦> count(column: \"_value\") | ¦> aggregateWindow(every: 1mo, fn: last, createEmpty: false) | ¦> filter(fn: (r) => r._value > 0, onEmpty: \"keep\")\n ¦> aggregateWindow(every: 1mo, fn: max, createEmpty: false)\n ¦> map(fn: (r) => ({ r with _value: r._value * 80.0 / 100.0})) | ¦> filter(fn: (r) => r._value > 0, onEmpty: \"keep\")\n ¦> aggregateWindow(every: 1mo, fn: mean, createEmpty: false)\n ¦> map(fn: (r) => ({ r with _value: r._value * 80.0 / 100.0}))
| object_unit | kW | kW |  | kW | kVA |  | kWh | °C | V | V | V |  | V
object_min_thresh
object_max_thresh
1 | Elmeasure Energy Meter(Distribution) | WHIMP | TKW | APF | TKW |  |  |  |  | AVLN | AVLN | IV1, IV2, IV3
2 | Elmeasure Energy Meter(Mains) | WHIMP | TKW | APF | TKW |  |  |  |  | AVLN | AVLN | IV1, IV2, IV3
3 | selec-306-C-D | KWH | TKW |  | TKW |  |  |  |  | V1N, V2N, V3N | V1N, V2N, V3N | IV1, IV2, IV3
4 | selec-mrj4m-quad | TKWH | TKW |  | TKW |  |  |  |  | V1N, V2N, V3N | V1N, V2N, V3N | IV1, IV2, IV3
5 | Schneider-Conzerv-METSEEM6438H | KWHEXP | TKW | APF | TKW |  |  |  |  | AVLN | AVLN | IV1, IV2, IV3
6 | schneider-em6400ng | KWH | TKW | APF | TKW |  |  |  |  | V1, V2, V3 | V1, V2, V3 | IV1, IV2, IV3
7 | Delta UPS |  |  |  |  | RKVA | [6 empty] | BATTVOLT | BATTVOLT | PLOAD | PLOAD
8 | some_model | [11 empty] | BATV | BATV | PLOAD | PLOAD
9 | sedemac_gc1111 | [5 empty] | HRS | KWH

## CO2
Sr No | Template Name | DEVICE_LEVEL_C02
| object_name | Devices C02
| footer_query | ¦> last()
object_unit
object_min_thresh
object_max_thresh
CO2

## TEMPERATURE
Sr No | Template Name | FLOOR_FEEL_TEMPERATURE | DEVICE_LEVEL_TEMP
| object_name | Floor feel temperature | Devices Temperature
| footer_query | ¦> filter(fn: (r) => r._value > 15 and r._value < 36, onEmpty: \"keep\")\n¦> group(columns: [\"_measurement\"])\n¦> mean(column: \"_value\") | ¦> filter(fn: (r) => r._value > 15 and r._value < 36, onEmpty: \"keep\") \n ¦> last()
| object_unit | °C | °C
object_min_thresh
object_max_thresh
|  | TEMP1 | TEMP1

## FIRE
Sr No | Template Name | PANEL_STATUS
| object_name | Panel Status
| footer_query | ¦> last()
object_unit
object_min_thresh
object_max_thresh
IN1